## Slide 1
SENSORS & DIGITAL TWIN
Iron Pellet Plant
Sensor Infrastructure,
Costs & Industry Benchmarks
AM/NS India · Vizag · 8 MTPA · Straight Grate Technology
For Digital Twin Deployment · 2025
320+
Sensors Deployed
₹12–18 Cr
Sensor CapEx
8 MTPA
Plant Capacity
7 Zones
Process Sections
Sensors • Process Control • Industrial IoT • Real-Time Analytics • Predictive Maintenance • AI/ML

## Slide 2
Process Sensor Architecture — 8 MTPA Pellet Plant
Sensor placement across 7 process zones | Total: 320+ instruments
OHP &
Stacker
38
sensors
Grinding
Mill
32
sensors
Slurry &
Filter
48
sensors
Green
Ball
28
sensors
Induration
Furnace
86
sensors
Cooler &
Screen
42
sensors
Quality
Lab
46
sensors
TEMPERATURE
94 units
· Thermocouple K-type (furnace)
· RTD Pt100 (slurry/cooler)
· IR Pyrometer (firing zone)
· Thermal Imaging Camera
PRESSURE
48 units
· Differential pressure transmitter
· Absolute pressure (vacuum)
· Manometric gauge + transmitter
· Draft pressure (furnace zones)
FLOW
42 units
· Electromagnetic (slurry, EM)
· Coriolis mass flow (fuel gas)
· Vortex (steam/air)
· Ultrasonic (water, clean liquid)
LEVEL & WEIGHT
36 units
· FMCW Radar (silos, tanks)
· Load cell / belt weigher
· Ultrasonic level gauge
· Nuclear gamma level (slurry)
QUALITY ANALYSIS
38 units
· On-line XRF (Fe, SiO₂, CaO)
· NIR moisture (belt/inline)
· Blaine fineness (laser)
· Vision system (PSD / shape)
VIBRATION & MOTION
62 units
· ICP accelerometer (bearings)
· WirelessHART vibration node
· Tachometer / speed encoder
· Acoustic emission (cracks)

## Slide 3
Zone 1 & 2: Raw Material Handling + Grinding Mill
OHP · Stacker Reclaimer · Silos · Blending · Ball Mill · Classifier — 70 Instruments Total
OHP & STACKER RECLAIMER
Sensor / Instrument | Specification | Qty | Unit Cost
Belt Weigher (4-idler frame) | ±0.25%, 500–2000 t/h range, 4-20mA | 3 | ₹8–12 L
Reclaimer Angle Encoder | Absolute, 0–360°, ±0.1°, IP65 | 4 | ₹2–4 L
Silo Level Radar (FMCW) | 80GHz, 0–30m, ±10mm, HART | 6 | ₹3–5 L
NIR Moisture (On-conveyor) | Near-infrared, 0–30%, ±0.3% | 2 | ₹15–22 L
Reclaimer Speed Tachometer | Inductive pulse, 0–500 rpm | 8 | ₹0.5–1 L
Bearing Vibration (ICP) | 3-axis, 0.5Hz–10kHz, IP67 | 6 | ₹3–6 L
Dust Opacity Monitor | Laser, 0–100%, 4-20mA | 4 | ₹6–10 L
Stockpile Load Cell | Compression 0–200t, ±0.1% | 5 | ₹1.5–3 L
GRINDING MILL & CLASSIFIER
Mill Vibration (ICP)
3-axis, 10Hz–10kHz, IP67
Mill Power Transducer
3-phase analyzer, ±0.5%
Mill Sound Level Meter
SPL 50–140 dB, 4-20mA
Blaine Fineness (On-line)
Laser diffraction, ±15 cm²/g
Classifier Speed Encoder
VFD feedback, 0–800 rpm
Inlet Temperature (RTD)
Pt100, 0–200°C, ±0.5°C
Water Flow (Mag EM)
DN50-100, 0.5–30m³/h, ±0.3%
Classifier Diff. Pressure
0–50 mbar, 4-20mA, HART
ZONE 1 & 2 COST SUMMARY
Belt scales + NIR moisture:
₹80–110 L
Vibration + encoders (18×):
₹65–100 L
Level radars + load cells (11×):
₹55–80 L
Grinding instruments (8×):
₹35–55 L
Zone 1+2 Total:
₹2.35–3.45 Cr
GRINDING ZONE
Blaine meter (on-line):
₹40–65 L
Vibration + power (8×):
₹20–35 L
Zone Total:
₹0.75–1.25 Cr

## Slide 4
Zone 3–5: Slurry Formation · Filtration · Green Ball Formation
Slurry circuit · Disc vacuum filter · Cake formation · Pugmill · Disc balling — 104 instruments
SLURRY & FILTRATION
Sensor | Specification | Qty | Cost
Density Meter (Coriolis/Nuclear) | Slurry 1.0–2.0 g/cm³, ±0.001 | 4 | ₹12–25 L
pH Analyzer (In-line electrode) | pH 0–14, ±0.02, 4-20mA | 4 | ₹1.5–3 L
Electromagnetic Flow Meter | DN50-150, ±0.3% FS, HART | 12 | ₹2–6 L
Viscosity Meter (Torsional) | 1–10,000 cP, IP67, 4-20mA | 2 | ₹8–15 L
Vacuum Pressure Transmitter | 0–1000 mmHg abs., SS316 | 6 | ₹1–2.5 L
Cake Moisture NIR (On-belt) | 0–25% moisture, ±0.3%, inline | 3 | ₹18–30 L
Filter Cloth Wear (Acoustic) | Acoustic emission, IPM 0–100% | 6 | ₹4–8 L
Slurry Temperature RTD | Pt100, 0–80°C, ±0.3°C, dip | 8 | ₹0.4–0.8 L
GREEN BALL FORMATION
Disc Inclination Sensor
0–60°, ±0.1°, IP65
On-line PSD Analyzer
Laser, 2–40mm, real-time
Green Burst Tester
Auto, 0–200N, statistical
Drum Speed Tachometer
Magnetic, 0–20rpm, IP65
Water Spray Flow (Coriolis)
0–50 l/h, ±0.1% FS
GB Moisture (On-belt NIR)
0–20%, ±0.2%, real-time
Bentonite Feeder Scale
Loss-in-weight, ±0.1%
Oversize Recycle Counter
Photoelectric, event+rate
SLURRY & FILTRATION COST
Density + pH + Flow meters:
₹85–120 L
NIR moisture + viscosity:
₹55–90 L
Vacuum + cloth monitors:
₹30–55 L
Zone 3–4 Total:
₹1.70–2.65 Cr
GREEN BALL ZONE COST
PSD Analyzer (on-line):
₹45–70 L
Disc + GB instruments (8×):
₹20–35 L
Zone 5 Total:
₹0.70–1.20 Cr

## Slide 5
Zone 6: Indurating Furnace — Critical Instrumentation (86 sensors)
Most sensor-dense zone · 7 thermal zones · Peak 1310°C · Fuel & emission monitoring critical
UDZ
280°C
6
DDD
410°C
6
PH-1
860°C
10
PH-2
1050°C
12
FIRING
1285°C
18
SOAKING
1260°C
12
COOL Z
850°C
8
Instrument | Specification | Qty | Unit Cost
Thermocouple K-type (Zone temps) | ASTM E230, 0–1400°C, ±2°C. Min 14 in firing. | 68 | ₹0.5–2 L
IR Pyrometer (Non-contact) | 0.85μm, 600–1600°C, fast response <1s | 8 | ₹8–18 L
Gas Flow Meter (Fuel, Coriolis) | ±0.1%, NG/BFG/LDO, 4-20mA+HART | 6 | ₹15–30 L
O₂ Zirconia Analyzer (In-situ) | 0–21%, response <5s, 4-20mA, ±0.1% | 8 | ₹8–15 L
CO/CO₂ Analyzer (NDIR) | 0–5% CO, 0–20% CO₂, MODBUS | 6 | ₹12–22 L
Waste Gas Pressure Transmitter | Differential, 0–500 mbar, HART, IP67 | 14 | ₹1–2.5 L
Grate Speed Resolver/Encoder | 0–5 m/min, 0.01mm resolution | 2 | ₹5–10 L
Bed Height Ultrasonic | 100–300mm, IP68, 4-20mA, ±1mm | 4 | ₹3–6 L
NOx Analyzer (UV-DOAS) | 0–500 mg/Nm³, ENS-certified | 2 | ₹25–40 L
Thermal Camera (Zone imaging) | 640×480 IR, 0–1500°C, Ethernet | 4 | ₹20–40 L
FURNACE ZONE TOTAL: ₹4.50–6.80 Cr | Thermocouples 68×: ₹0.80–1.36 Cr | Gas Analyzers 22×: ₹2.64–4.06 Cr | Thermal Cameras 4×: ₹0.80–1.60 Cr

## Slide 6
Total Sensor Investment — 8 MTPA Pellet Plant
Capital expenditure estimate · Process instrumentation only · Excludes DCS/SCADA/network
TOTAL SENSOR
CAPEX
₹ 12 – 18 Cr
Complete 8 MTPA pellet plant
320+ instruments · 7 zones
Zone | Sensors | Low (₹ Cr) | High (₹ Cr)
OHP & Stacker Reclaimer | 38 | ₹ 1.63 | ₹ 2.73
Grinding Mill & Classifier | 32 | ₹ 0.75 | ₹ 1.25
Slurry & Disc Filtration | 48 | ₹ 1.70 | ₹ 2.65
Green Ball Formation | 28 | ₹ 0.70 | ₹ 1.20
Indurating Furnace | 86 | ₹ 4.50 | ₹ 6.80
Circular Cooler & Screening | 42 | ₹ 0.95 | ₹ 1.65
Quality Control Lab | 46 | ₹ 2.18 | ₹ 3.92
★ TOTAL | 320+ | ₹ 12.41 | ₹ 20.20
Chart: 
| OHP+Grind | Slurry+Filter | Green Ball | Furnace | Cooler+Screen | Quality Lab
Cost % | 2.18 | 2.23 | 0.95 | 5.65 | 1.3 | 3.05
ADDITIONAL INFRASTRUCTURE (All-In Digital Twin)
DCS/PLC upgrades: ₹2–4 Cr
IoT gateways + edge compute: ₹1.5–3.2 Cr
Network (fiber+switches): ₹0.8–1.5 Cr
AI/ML software platform: ₹1–3 Cr
Engineering + commissioning: ₹2–4 Cr
ALL-IN TOTAL:
₹20–35 Cr

## Slide 7
Global Pellet Plant Digital Twin Deployments — Peer Industry Benchmarks
Where iron pellet plant sensor networks & digital twins are deployed today
LKAB (Sweden)
Scandinavia · 28 MTPA
Grate-Kiln
Digital twin operational since 2018 at Malmberget & Kiruna. Full sensor network with online XRF, thermal cameras, and acoustic monitors. Autonomous burn-control AI closed-loop since 2021.
Sensors: 500+ sensors · On-line XRF · Thermal imaging · Vision PSD · WirelessHART vibration
Impact: 8–12% fuel saving · ±2 daN CCS accuracy · 30% maintenance cost reduction
Siemens SIMATIC + AVEVA
Vale (Brazil)
Tubarão, São Luís · 60 MTPA
Straight Grate
Digital replica at Tubarão (SV) & São Luís plants. Connected to autonomous mine-to-port digital thread. AI quality prediction for DRI pellet specification compliance.
Sensors: 800+ sensors · On-line WDXRF · Coriolis fuel · Thermal cameras · Vibration mesh
Impact: 6–8% energy reduction · +7% quality yield improvement · Maintenance ROI 3.2×
Rockwell Automation + Aspen Tech
Cleveland-Cliffs (USA)
Minorca + Tilden · 20 MTPA
Straight Grate
IIoT platform deployed 2019–2022 across all pellet plants. EPA CEMS-compliant gas monitoring. Machine learning quality prediction integrated into furnace PLC control.
Sensors: 320+ sensors · Gas CEMS (CO, NOx, SO₂) · Thermal profiling · Level + weighers
Impact: 4–6% production increase · Emission compliance cost −25% · OEE +3%
GE Vernova + Emerson DeltaV
Samarco (Brazil)
Germano / Ubu · 22 MTPA
Straight Grate
Full digital twin post-2019 re-commissioning. CCS prediction model integrated real-time with furnace setpoints. Closed-loop basicity control via online XRF.
Sensors: 400+ instruments · On-line CCS prediction · XRF basicity control · Gas analysis
Impact: 9% CCS improvement vs pre-restart · −7% energy · Fuel curve optimization
ABB 800xA + Honeywell
Jindal Steel & Power
Odisha, India · 8 MTPA
Straight Grate
Industry 4.0 upgrade 2021–23. Level-2/3 automation integrated with digital historian. On-line quality monitoring. Targeting full DT by 2025.
Sensors: ~250 sensors · Gas analysis · Belt weighers · On-line moisture · Basic quality
Impact: 3–5% productivity gain · Energy monitoring established · Targeting 6% reduction
Siemens SIMATIC PCS 7
KIOCL Ltd (India)
Mangalore · 3.5 MTPA
Straight Grate
Partial automation upgrade complete. MECON-assisted digital integration. Full sensor upgrade planned 2024–25 under National Steel Policy digitalization mandate.
Sensors: ~120 sensors currently · Target 300+ · Thermocouples + basic flow+level
Impact: In progress · Targeting 5–8% energy reduction · MECON feasibility study done
BHEL + Siemens (planned)

## Slide 8
Sensor Vendor Ecosystem & Technology Selection Guide
Recommended suppliers by category · OEM benchmarks · India availability
TEMPERATURE
Endress+Hauser
iTHERM TM411, Pt100/K-type, HART/4-20mA. India: Mumbai. Used SAIL, JSPL.
ABB Measurement
TSP300 thermocouples, ±0.1°C, SIL2. Deployed LKAB, Vale furnaces.
Jumo (Germany)
DELOS L series up to 1400°C. India distributor: Elicab Controls, Pune.
Pyromation / Drager
High-temp IR pyrometers for firing zone >1200°C. Non-contact.
GAS ANALYSIS
ABB AO2020
Multi-gas O₂/CO/CO₂, MODBUS/PROFIBUS. Industry standard pellet furnaces.
Emerson Rosemount 6888
In-situ zirconia O₂ probe, direct insertion, <5s response, ±0.1%.
SICK MERZ CEMS
Continuous emission monitoring, NO/NOx, ENS/TÜV certified. India: Gurgaon.
Yokogawa TDLS8000
Tunable diode laser, CO/NH₃/HF. Furnace atmosphere direct measurement.
FLOW MEASUREMENT
Endress+Hauser Promag
Electromagnetic flow, slurry-rated, ±0.3%. Most-used in India pellet plants.
Yokogawa ROTAMASS
Coriolis mass flow for fuel gas, ±0.1%, direct mass not volume.
Krohne OPTISONIC
Ultrasonic gas flow, custody transfer, DN50–DN600, clamp-on option.
Siemens MAG 5100W
Water-cooled electrodes for high-temp abrasive slurry up to 80°C.
LEVEL & WEIGHT
VEGA VEGAPULS 69
80GHz FMCW radar, ±2mm, silo/tank. IP68. Used KIOCL, JSPL silos.
Schenck Process / Siemens
Belt weighers MSI, 4-idler, ±0.25%. Most-used belt scale India.
Berthold (Nuclear)
Gamma density/level for slurry tanks. Non-contact, no process penetration.
Sartorius / Mettler Toledo
Loss-in-weight feeders for bentonite dosing. ±0.1% accuracy.
QUALITY / XRF / VISION
Thermo Fisher CrossBelt XRF
On-belt XRF, Fe/SiO₂/CaO/Al₂O₃. LKAB, Vale, Samarco deployed.
Malvern Panalytical
Epsilon XRF + Mastersizer PSD laser. Standard for quality lab.
NDC Technologies (NIR)
On-belt NIR moisture gauges, ±0.1%, pellet & filter cake.
Cognex / Keyence Vision
AI vision for pellet size, shape detection on conveyor belt.
VIBRATION & CBM
SKF Multilog IMx
Online bearing monitor, vibration+temp, PROFIBUS. Used mill, fans, grate.
Emerson AMS 9420
WirelessHART vibration, 2-year battery. Saves 30% cable installation cost.
Brüel & Kjær (HBK)
High-freq ICP accelerometers, mill sound & body vibration analysis.
National Instruments cDAQ
Custom data acquisition for multi-channel vibration + motor signature.

## Slide 9
AM/NS India Digital Twin — Phased Sensor Deployment Roadmap
4-phase implementation · Total 42 months · Phased CapEx · KPI milestones at each phase
Phase 1
0–6 months
Foundation Sensors
· Belt weighers + radar level (OHP)
· Thermocouple upgrade (Furnace 68 TCs)
· Gas analyzers O₂/CO (6+6 units)
· Belt NIR moisture + conveyor sensors
· DCS integration + process historian
₹4–6 Cr
Energy baseline · Fuel monitoring
Phase 2
6–18 months
Quality & Analytics
· On-line XRF analyzer (cross-belt)
· Slurry density + pH + EM flow (full)
· Disc filter moisture + cloth monitor
· Blaine fineness on-line (laser)
· Edge compute + IIoT gateways deployed
₹4–7 Cr
CCS ±8 daN · Energy −5%
Phase 3
18–30 months
Predictive & AI
· Vibration monitors (all rotating equip)
· Thermal cameras (furnace, 4 units)
· Vision system (pellet PSD / conveyor)
· ML models: quality + energy + fault
· Digital twin real-time sync active
₹4–6 Cr
Predictive maint. ROI 3× · PSD AI
Phase 4
30–42 months
Autonomous Optimization
· Closed-loop AI control (furnace auto)
· Autonomous grate speed + fuel opt.
· WHR steam optimization controller
· Integrated plant-level optimizer AI
· Operator training via digital twin
₹2–4 Cr
8–12% energy saving · Closed loop
Tech Stack: Siemens SIMATIC / ABB 800xA DCS · AVEVA PI Historian · AWS IoT / Azure IoT Hub · Python ML · PROFIBUS-PA / HART / WirelessHART / OPC-UA · MODBUS TCP

## Slide 10
ROI Analysis & Peer Industry Performance Benchmarks
LKAB · Vale · Cleveland-Cliffs · Samarco · JSPL published performance data · 2019–2024
5–12%
Energy Cost Reduction
Fuel optimization AI control
3–5×
Maintenance ROI
Predictive vs reactive maint.
2–3 yrs
Full Payback Period
Sensor + DT total investment
₹45–80 Cr
Annual Savings (8 MTPA)
Energy + quality + maintenance
Company | Energy Saving | CCS Improvement | Maint. Saving | Payback | DT Maturity
LKAB (Sweden) | 8–12% | ±4→±2 daN | 30–40% | 2.1 yrs | ★★★★★ Full
Vale (Brazil) | 6–8% | CCS yield +7% | 25–35% | 2.5 yrs | ★★★★★ Full
Cleveland-Cliffs | 4–6% | ±6→±3 daN | 20–28% | 3.0 yrs | ★★★★ Advanced
Samarco (Brazil) | 7–9% | CCS +9% | 22–30% | 2.8 yrs | ★★★★ Advanced
Jindal Steel | 3–5% | ±5 daN improv. | 15–20% | 3.5 yrs | ★★★ Growing
AM/NS India (Target) | 6–10% | ±4 daN target | 25–35% | 2.5 yrs est. | ★★★ → ★★★★★
Chart: 
| LKAB | Vale | Cliffs | Samarco | JSPL | AM/NS tgt
Energy Saving (%) | 10 | 7 | 5 | 8 | 4 | 8
CCS Improvement (%) | 8 | 7 | 5 | 9 | 5 | 7

## Slide 11
Digital Twin Sensor Summary — AM/NS India Vizag · 8 MTPA
From raw material to dispatch · 320+ sensors · ₹12–18 Cr CapEx · Full payback in 2.5 years
01
Furnace is the Priority
86 sensors in indurating furnace alone (27% of total). Gas analyzers, TCs, and thermal cameras deliver highest ROI through fuel optimization of 4–12% cost reduction.
02
On-line XRF is Critical
Continuous Fe/SiO₂/CaO measurement enables closed-loop basicity control. LKAB and Vale credit on-line XRF for CCS consistency improvement of ±4 → ±2 daN.
03
Phase Your Investment
Start with TCs + gas analyzers + belt weighers (Phase 1, ₹4–6 Cr). Add quality analytics Phase 2. Full AI closed-loop in Phase 3–4 over 42 months.
04
2.5 Year Payback Industry Avg
LKAB full payback in 2.1 years. Vale: 2.5 yrs. Cleveland-Cliffs: 3.0 yrs. Proportional annual savings: ₹45–80 Cr at 8 MTPA operation.
05
WirelessHART Reduces Cost
Emerson AMS 9420 wireless vibration saves 20–35% installation cost vs wired. Key for rotating equipment — mills, fans, cooler drives — where cabling is expensive.
06
Indian Vendor Ecosystem Ready
E+H, ABB, Siemens, Yokogawa have India offices and spares warehouses. BHEL + MECON provide DCS/SCADA integration. Import lead times: 8–14 weeks.
AM/NS India Digital Twin Program · Vizag · 8 MTPA · Confidential · 2025
Sources: LKAB Annual Report | Vale Technology | Emerson | E+H | ABB | MECON Technical Reports